## German
| Category | Description | Name_Digital_Application | Projektname | Funding_Label | Duration | Partner | Project_Website | Consortium | Further | Digital_applications | Goals | Strategies | Relevance | Image | Problem_Statement_and_Problem_Goals | Implementation_in_the_Project | Evaluation | Project_Name | Weiterführende Literatur
0 | Positive Wirkung | Das Projekt RLT-Opt adressiert das Problem ineffizienter raumlufttechnischer Anlagen (RLT-Anlagen) in deutschen Nichtwohngebäuden. Der Projektverbund schätzt, dass die ca. 400.000 Teilklima- und 600.000 mittleren bzw. großen Lüftungsanlagen im Gebäudebestand etwa 40 TWh/a Strom verbrauchen, was ca. 8 % des deutschen Gesamtverbrauchs ausmacht (Stand: 2022). | RLT-Opt | RLT-Opt – Lüftungs- und Klimaanlagen ganzheitlich optimieren | 03EN1037A | 04/2021–03/2024 | FraunhoferIOSB, BUILDING Consultants + Innovators GmbH, IBDM GmbH, Effizienzbörse Deutschland GmbH | www.rlt-opt.de | https://www.iosb.fraunhofer.de/de/projekte-produkte/rlt-opt-lueftungsanlagen-klimaanlagen-optimieren/konsortium.html | https://effizienzboard.de | Betriebsoptimierung, Dashboards | Informationsvermittlung, Energieeffizienzsteigerungen, Verbrauchs- und Kostenminimierung, Lebensdauerverlängerung | Informations- und Wissensvermittlung; Austausch von Geräten; Manuelles Einstellen von Geräten; Frühzeitige Fehlererkennung | Hohe positive Umweltwirkungen (Energieeinsparungen) | img/componentList/environment-positive.svg | Das Projekt RLT-Opt adressiert das Problem ineffizienter raumlufttechnischer Anlagen (RLT-Anlagen) in deutschen Nichtwohngebäuden. Der Projektverbund schätzt, dass die ca. 400.000 Teilklima- und 600.000 mittleren bzw. großen Lüftungsanlagen im Gebäudebestand etwa 40 TWh/a Strom verbrauchen, was ca. 8 % des deutschen Gesamtverbrauchs ausmacht (Stand: 2022). Trotzdem ist die Anzahl an Anlagen, bei denen energetische Inspektionen durchgeführt wurden, gering (etwa 25.000 Anlagen). Bei diesen Anlagen werden häufig hohe Energieeinsparpotenziale durch die Optimierung der Wärme-, Kälte-, und Stromverbräuche identifiziert. Grundsätzlich liegen jedoch bisher zu wenig Daten zu den Betriebsständen von RLT-Anlagen vor, da bei Anlagenerrichtung häufig auf Monitoring-Komponenten verzichtet wird. Hinsichtlich der energetischen Inspektionen von RLT-Anlagen wurde bereits in älteren Studien für ca. 50% aller Anlagen eine optimierte Regelstrategie und für ca. 40% der Anlagen eine Erweiterung der Sensorik empfohlen, um so Einsparpotenziale zu heben. Das Hauptproblem besteht folglich darin, dass bei den meisten Anlagen unklar ist, ob der Energieverbrauch im Betrieb notwendig für das Erreichen der gewünschten Ziele wie bspw. einer bestimmten Lüftungsleistung ist. Hier setzt das Projekt an und zielt darauf ab, mittels eines mobilen und stationären Monitoringkonzepts Schwachstellen in RLT-Anlagen zu analysieren, Einsparpotenziale zu identifizieren, ableitende Kennzahlen zu ermitteln und diese anwender*innennah darzustellen. Durch diese Maßnahmen soll daraufhin der Betrieb optimiert und Energie, Kosten und CO2 eingespart werden. Weitere Ziele, die mit dem optimierten Anlagenbetrieb einher gehen, umfassen die Steigerung der Ressourceneffizienz und die Verlängerung der Lebensdauer der RLT-Anlagen. Mit der Anwendung des mobilen Monitoringsystem, welches zeitlich begrenzt eingesetzt wird und auf einem geringen Materialinput basiert, können bereits hohe positive Umweltwirkungen verbunden sein. Die gesammelten Daten werden z.B. in Excel-Checklisten aufbereitet und ausgewertet, sodass Anlagenbetreiber*innen bereits frühzeitig fundierte Entscheidungen treffen können (z.B. Anpassung des Betriebs, Austausch von Komponenten/Anlagen etc.). Für das umfangreicherer stationäre Monitoringsystem setzt das Projekt auf Dashboards als strategisches Instrument zur Informationsvermittlung. Durch Infografiken zu Betriebszuständen und Aufarbeitung von Kennzahlen sollen Betreibende von Anlagen, Gebäudeleittechniker*innen und Energiemanager*innen dazu befähigt werden, den Anlagenbetrieb eigenständig und fortlaufend energiesparend anzupassen. Die Optimierung des Betriebs erfolgt beispielsweise durch bedarfsgerechte Anpassung der Betriebszeiten, der Volumenströme der RLT-Anlagen sowie von Schwellwertparametern, welche für die Aktivierung/Deaktivierung von bestimmten Betriebsmodi wesentlich sind. Konkret wurden im Projekt vier unterschiedliche Liegenschaften als Demonstrationsgebäude untersucht: zwei kleine Industriebetriebe, ein Krankenhaus und ein großer Bürogebäudekomplex. Dementsprechend ist auch die verbaute Technik sehr unterschiedlich und verschieden komplex. Auch die Kommunikation und Aufgabenteilung der beteiligten Personen seitens der Liegenschaften ist stark heterogen: Bei den größeren Liegenschaften fehlt häufig der Kontakt zu Expertiseträger*innen: Während bei kleineren Liegenschaften Ansprechpartner*innen mit umfassenden Kompetenzen und Aufgaben leichter zu erreichen sind und bei Bedarf auch auf die Anlagen zugegriffen werden kann, erweist sich dies bei den größeren häufig als schwierig. | Im Rahmen des Projekts wurden verschiedene Ansätze verfolgt, um Potenziale zu heben und die Effizienz der raumlufttechnischen Anlagen zu steigern. Eine zentrale Stellschraube war die einfache Regelungsoptimierung nach den Normen DIN EN 15232 und ISO 52120. Hierbei erfolgte eine Gesamtsystembetrachtung, um den Volumenstrom des Ventilators aus Basis eines Soll-Ist-Vergleichs zu minimieren. Bedarfsgerechte Anpassungen der Betriebszeiten und Volumenströme im fortlaufenden Betrieb wurden ebenfalls umgesetzt. Zusätzlich wurden umfangreichere Optimierungsmaßnahmen auf Grundlage von Monitoring-Daten durchgeführt, um beispielsweise gleichzeitiges Heizen und Kühlen zu verhindern. <br><br> Für die technische Umsetzung kamen zwei Varianten des Monitorings zum Einsatz. Ein mobiles Monitoring wurde zur Erfassung und Bewertung des Status-Quo genutzt, während ein stationäres Monitoring mit festverbauten Komponenten zusätzliche Einblicke in den Betrieb und eine kontinuierliche Betriebsoptimierung ermöglichte. Das mobile Monitoring erfordert weniger Komponenten. Der Ressourcen-Energiebedarf der Technik für das mobile Monitoring wird im Projekt als sehr gering eingeschätzt. Er beläuft sich auf wenige zusätzliche Sensoren und Zähler. Nichtsdestotrotz lassen sich bereits mit dem mobilen Monitoring enorme Einspareffekte erzielen, insbesondere in Bezug auf die Funktionalität und Dimensionierung der Anlagen bzw. deren Betriebsparameter. <br><br> Die Implementierung des stationären Monitorings erforderte wiederum zusätzliche Hardware und einen höheren Datenaufwand. Dabei gilt grundsätzlich, dass Art und Anzahl der zusätzlich notwendigen Komponenten stark von der Größe und Grundausstattung der Liegenschaft sowie von den dortigen Anlagen abhängt. Mit der Aufnahme detaillierter Betriebszustände sind dann jedoch tiefergehende Analysen möglich, mit denen weitere Einsparpotenziale erst erschlossen werden können. | Als positive Umweltwirkungen wurden im Projekt vor allem Energie- und CO2-Einsparungen angestrebt. Die Quantifizierung dieser Wirkungen wurde mittels eines Vorher-Nachher-Vergleichs tatsächlicher Energiemengen versucht, der sich auf unterschiedliche Zeiträume erstrecken kann (in Abh. des jeweiligen Monitoringkonzepts – mobil und/oder stationär). Im Allgemeinen wurden Kennwerte zur Anlagenbewertung in Anlehnung an DIN SPEC 15240 und DIN 18599 gebildet. Einsparungen wurden teilweise messtechnisch nachgewiesen und teilweise über Hochrechnungen nach allgemeinen physikalischen Regeln bewertet, wobei um Wettereinflüsse gewichtete Bereinigungen vorgenommen wurden. Darauf aufbauend wurden die CO2-Einsparungen ausgehend von den, vom Bundesamt für Wirtschaft und Ausfuhrkontrolle veröffentlichten, Emissionsfaktoren für Energieaudits berechnet.<sup id="ref1"><a href="#footnote1">1</a></sup> <br><br> Die erzielten Ergebnisse der Optimierung nach den Normen DIN EN 15232 und ISO 52120 waren bemerkenswert mit durchschnittlichen Stromeinsparungen von durchgängig > 30 %. Gerade das grundsätzliche Einstellen des Volumenstroms (Soll-Ist Abgleich, Anpassen der Betriebszeiten etc.) stellt dabei eine einfach umzusetzende Maßnahme dar, welche sich bereits unter Einsatz des mobilen Monitorings – also unter minimalen Einsatz von Messtechnik und Ressourcen – durchführen lässt. Bei einigen Anlagen können die somit erzielten Einsparungen auch noch deutlich höher als die mittleren 30 % ausfallen. Denn bereits bei einer Verringerung des Volumenstroms um 20 % halbiert sich die Leistungsaufnahme. So konnte der Volumenstrom für die Belüftung des Kellerbereichs einer Beispielliegenschaft um 39 % gesenkt werden, was eine Reduktion des Strombedarfs um 78 % bewirkte. Jährlich können somit ca. 270 MWh bzw. 198 tCO2eqeingespart werden. Mit der Feinjustierung der Anlagen in Abhängigkeit der Raumbelegung/Raumnutzung lassen sich dann weitere Effizienzpotenziale erschließen. Dafür wird jedoch das stationäre Monitoring notwendig, da längere Zeiträume betrachtet werden müssen. Eine weitere positive Umweltwirkung die mit der Optimierung des Betriebs einhergeht: durch die geringe Nutzung, verschleißen die Anlagen auch weniger. Dadurch kann die Lebensdauer deutlich gesteigert werden. Der Projektverbund geht hier von möglichen Lebensdauersteigerungen von bis zu 10 Jahren aus. Ressourcen werden somit länger genutzt und Emissionen vermieden. Ebenso wird die Fehlererkennung vereinfacht bzw. verfrüht, was dazu führen kann, die Anlagen schneller und effektiver zu warten bzw. instand zu halten. Negative Umweltauswirkungen der digitalen Anwendungen wurden nicht mit in die Bilanz einbezogen. Je nach vorhandener Anlagentechnik und Gebäudeleittechnik fallen die Emissionen, hervorgerufen durch das Monitoring sowie die Datenverarbeitung, in den einzelnen Liegenschaften unterschiedlich hoch aus. Am Beispiel des großen Bürogebäudekomplexes (größte untersuchte Liegenschaft): hier wurden über hundert zusätzliche Sensoren (Lufttemperatur, Bestrahlungsstärke, Luftfeuchte, Präsenzmelder, CO2, Druck) ca. 50 Zähler (Strom, Volumenstrom, Wärmemengen), mehrere Kommunikationssysteme (BUS-Systeme, Router, Repeater, Laptops) und mehrere hundert Meter Kabel (Strom, Luft, LAN) für das stationäre Monitoring zusätzlich installiert. Insgesamt entsteht bei dieser Liegenschaft ein Datenaufwand von 10 GB/Jahr. Bei solchen, vergleichsweise komplexen, Liegenschaften kann es zudem zu weiteren Hürden kommen, die die Effektivität der Maßnahmen verringern können. Hier ist vor allem die Gebäudeleittechnik bzw. deren Zugänglichkeit (geschlossene Schnittstellen, Fehlen der Expert*innenebene) zu nennen, welche die Umsetzbarkeit der Handlungsempfehlungen zur Betriebsoptimierung erschweren kann. Prädiktive Regelstrategien, die ggf. noch höhere Einsparpotenziale mit sich bringen würden, sind somit oftmals nur kostspielig umsetzbar. Gleichzeitig ist es sinnvoll, die Anlagenbetreiber*innen bei der Umsetzung der möglichen Betriebsoptimierungsstrategien (z.B. manuelles Einstellen des Volumenstroms oder der Betriebszeiten) zu unterstützen, da sich im Projekt zeigte, dass diesbezüglich z.T. wenig Expertise und vorherige Berührungspunkte existieren. Trotz der materiellen Aufwände und technisch-organisatorischen Hürden, konnten auch bei großen Liegenschaften Stromeinsparungen von durchgängig > 30 % realisiert werden. | RLT-Opt– Lüftungs- und Klimaanlagen ganzheitlich optimieren | <sup id=”sup1”><a href="#ref1">1</a></sup> Basis für Berechnung: Emissionsfaktor Strom (Effizienzmaßnahmen) = 0,732 tCO2/MWh, aus Informationsblatt CO2-Faktoren; Bundesamt für Wirtschaft und Ausfuhrkontrolle, 2021.
1 | Positive Wirkung | Der Fokus des Projekts liegt insbesondere auf der Energieeffizienzsteigerung von Heizungs-, Kühlungs- und Klimasysteme in Bürogebäuden unter Berücksichtigung der Zufriedenheit der Nutzenden. Zum Einsatz kommt dabei eine Modell-prädikative Regelung (engl. Model Predicitve Control (MPC)), die es ermöglicht, nicht-lineares Systemverhalten vorauszusagen und automatisiert zu steuern. Verschiedene Studien beziffern die Energieeinsparungen zwischen 15 % und 50 % (Mork et al. 2023). | LLEC | LLEC – Verwaltungsbau: Klimaneutraler Verwaltungsbau als aktiver Teil des Living Lab Energy Campus; EnOB: LLEC: Living Lab Energy Campus | 03EGB0010A;; 03ET1551A | 01/2018 – 06/2025, 01/2018 – 03/2025 | Karlsruher Institut für Technologie, LOHC Technologies, Zulieferer: BFT Planung GmbH, Hydrogenious, Riello Power Systems GmbH, AutoPi.io ApS, be.storaged GmbH, SonnJa! GmbH | https://www.fz-juelich.de/de/llec |  |  | Betriebsoptimierung, Dashboards, Digitaler Zwilling | Energieeinsparungen, Verbrauchsminderung, Komfortsteigerung | Steuerung- und Regelung / Model Predictive Control, Gamification, Informations- und Wissensvermittlung | Verbrauchsreduktion in komplexe Gebäudestrukturen u.a. durch die Nutzenden | assets/images/llec_logo_large_transparent.png | Die Heterogenität von Gebäuden, die beispielsweise durch unterschiedliche Anlagenparks und/oder Nutzungsprofile entsteht, sowie das Verhalten der Nutzenden von Gebäuden stellen komplexe Herausforderungen zur Minimierung des Energieverbrauchs dar. Oftmals fehlen verlässliche Daten und entsprechende digitale Anwendungen, um den Energieverbrauch und die Effizienz von Gebäuden angemessen zu bewerten und zu optimieren. Durch ihren erheblichen Anteil am Gesamtenergieverbrauch (30 %) steht die Verbesserung der Energieeffizienz und Reduzierung von CO2-Emissionen von Gebäuden zunehmend im Fokus derzeitiger Forschung <a href="#United_Nations_Environment_2021">(United Nations Environment Programme 2021)</a>. <br><br> Das Living Lab Energy Campus (LLEC) am Forschungszentrum Jülich verfolgt das Ziel, Lösungen für die Energieeffizienz in Gebäuden zu erforschen und der Öffentlichkeit vorzustellen. Hochgradig vernetzte Demonstratoren zeigen verschiedene Forschungsarbeiten, beispielsweise zu Photovoltaik oder der Energiespeicherung. Außerdem wird in zwei Projekten versucht, durch die Integration innovativer Technologien und Ansätze den Energieverbrauch zu minimieren. Zentraler Schlüssel ist dabei die Erfassung und Analyse von Gebäudedaten. Darauf aufbauend werden modulare Lösungen entworfen, die nach erfolgreicher Testung auch auf andere Gebäude übertragen werden können. Ein Schwerpunkt der Optimierung ist diesbezüglich die Entwicklung intelligenter Regelung zur Steuerung von Energieverbrauchsanlagen in einigen Gebäuden und der Energiedemonstratoren des Campus. Um der hohen Heterogenität der Gebäude bzw. Gebäudeteile zu begegnen, muss dabei eine Vielzahl an Einflussgrößen betrachtet werden. Parallel dazu wird in einem anderen Gebäude das Nutzerverhalten als aktives Mittel zur Verbrauchsminimierung erforscht und genutzt. Das LLEC ermöglicht die Entwicklung und Anwendung solcher Lösungen in einem repräsentativen und realistischen Umfeld, das Validierung von Forschungsergebnissen ermöglicht. Insbesondere im Verwaltungsbau kann die Einwirkung auf die intrinsische Motivation von Personen essentiell sein, da sie sich nachgewiesenermaßen nicht für ihren Einfluss auf Energieverbrauch verantwortlich fühlen, solange sie die Kosten nicht tragen. Ein weiteres Ziel des Projekts ist die Förderung des Wissenstransfers und die Sensibilisierung für das Thema Energieeffizienz in Gebäuden. Das LLEC bietet dazu Schulungen, Workshops und Informationsveranstaltungen für Fachleute, Studierende und die interessierte Öffentlichkeit an, um das Bewusstsein für energieeffizientes Bauen zu stärken und Fachwissen zu verbreiten. | Der Fokus des Projekts liegt insbesondere auf der Energieeffizienzsteigerung von Heizungs-, Kühlungs- und Klimasysteme in Bürogebäuden unter Berücksichtigung der Zufriedenheit der Nutzenden. Zum Einsatz kommt dabei eine Modell-prädikative Regelung (engl. Model Predicitve Control (MPC)), die es ermöglicht, nicht-lineares Systemverhalten vorauszusagen und automatisiert zu steuern. Verschiedene Studien beziffern die Energieeinsparungen zwischen 15 % und 50 % <a href="#Mork,_Maximilian,_Florian_2023">(Mork et al. 2023)</a>. Im Projekt berücksichtigt die praktisch umgesetzte MPC den Energieverbrauch für Heizung und Beleuchtung, thermisches Unbehagen, sowie potenzielle Nutzer-Störungen durch hochfrequentes Fahren der Verschattung. Die Steuerung erfolgt unter Rücksichtnahme auf Abstimmungsparameter und Komfortgrenzen. Es ist zu erwähnen, dass für die Nutzung der MPC derzeit eine maßgeschneiderte Modellierung für jedes individuelle Gebäude notwendig ist, aber auch in diesem Projekt an Vereinfachungen gearbeitet wird (z.B. einfach zu erstellende und übertragbare Modelica-Module). Bezüglich des Einflusses des Wetters wurden unterschiedliche Effekte wie Außentemperaturen / Heizbedarfe, Windstärken und solare Gewinne mit in die Steueralgorithmen einbezogen. <br><br> Unabhängig von den Ansätzen zur MPC, beschäftigen sich die Forschenden mit der Integration von Softwareanwendungen, die es ermöglichen, Energieverbrauchsdaten einzusehen und den Nutzenden Echtzeitempfehlungen für Verhaltensänderungen zu geben <a href="#Ubachukwu,_Eziama,_Jana_2023">(Ubachukwu et al. 2023)</a>. Das „Energy Dashboard“ bietet Mitarbeitenden und Besucher*innen des LLEC u.a. auf Raumlevel einen Überblick über Heiz- und Stromverbrauch in Echtzeit. „JuControl“ geht eine Ebene weiter und ermöglicht es den Nutzenden, ihre persönlichen Präferenzen für das Raumklima abzubilden und in die Steuerung einzugreifen. In die Anwendung ist dabei ein Gamification Ansatz eingebettet, der den Vergleich mit anderen Personen/Teams ermöglicht. Das Feedback an die Nutzenden erfolgt über ein Ampelsystem, das den Energieverbrauch angibt. Die Bewertung der Ampel erfolgt anhand festgelegter Grenzen, gemessen in Kilowattstunden. Außerdem spiegelte die Anwendung einen “Energiestrafwert” wider, der simuliert wie hoch der Energieverbrauch des gesamten LLEC Campus gewesen wäre, wenn alle Personen ein entsprechendes Nutzungsprofil gehabt hätten (Idealwert). In diesem Sinne grenzt sich das Projekt von herkömmlichen Ansätzen zur Bewertung der positiven Umweltwirkungen ab. Während normalerweise die Einsparung in Referenz zum Status-Quo-Verbrauch gesetzt wird, fragt die Referenz am LLEC nach dem Idealzustand, der erreicht werden könnte. Denn je nach Lage, Nutzungsart und persönlichen Erfahrungen der Nutzenden, können die Möglichkeiten zu Energieeinsparungen in Einzelräumen stark variieren. Durch die Definition eines Ideals wird diesen Einflüssen Rechnung getragen. Ergänzt wird das System zur Nutzendeneinbindung durch ein Leaderboard (in der Anwendung „JuPower“), das Teams mit dem niedrigsten Energieverbrauch auszeichnet. Anreize für energieeffizientes Verhalten der Nutzenden wird zudem durch soziale Interaktion und „game rewards“ geschaffen. <br><br>Um die korrekte Messung der Daten zu gewährleisten wurden in allen teilnehmenden Gebäuden Sensoren des Typs EnOcean zur Messung der Luftqualität, der CO2 Konzentration, Temperatur und Feuchtigkeit verbaut. Die Verarbeitung der Daten erfolgte mit M-Bus. Zur automatischen Steuerung von Beleuchtung, Heizung und Sonnenschutz kamen KNX Steuerelemente und BACnet-Systeme zum Einsatz. Über den gesamten Campus des LLEC wurden Untersuchungen zur Integration von über 1800 Geräten in 18 Gebäuden mittels einer Informations- und Kommunikationsplattform durchgeführt (EnOcean: 1676 Sensoren und 108 Aktuatoren, KNX: 48 Sensoren und 36 Aktuatoren) <a href="#Althaus,_Philipp,_Florian_2022">(Althaus et al. 2022)</a>. | Die Forschenden schätzen die Energieeinsparungen, die mittels MPC erreicht werden können, über sämtliche getestete Gebäude auf ca. 10 – 15 %. Dazu wurde ein digitaler Zwilling der Gebäude mittels unterschiedlicher Regelstrategien vergleichend betrieben. Den größten Einfluss auf die Energieeinsparungen haben dabei das intelligente Steuern der Raumtemperatur, der automatisierten Fensteröffnung sowie das Anpassen des Sonnenschutzes (Fokus Wärme/Klimatisierung; Auswirkungen auf Strombedarf für Beleuchtung nicht inkludiert). Der Sonnenschutz ist so ausgelegt, dass ein Maximum an solaren Wärmegewinnen und Tageslicht nutzbar gemacht werden kann, um den Energieverbrauch für Heizung und Beleuchtung zu minimieren. Die messtechnische Überprüfung konnte die Simulationen qualitativ bestätigen. So wurden energieeffizientere Raumtemperaturprofile gemessen. Ein genauer Vergleich des Energieverbrauchs konnte jedoch auf Grund mangelnder Zähler in den einzelnen Räumen / Gebäudeteilen nicht zielführend durchgeführt werden. Quantitativ kann das LLEC die hohe Genauigkeit des white-box MPC-Modells bestätigen. Der Root Mean Square Error (RSME) zwischen gemessener und geschätzter Raumtemperatur lag bei 0,49 °C. Zudem konnte die effiziente Arbeitsweise der Regelung belegt werden. Im Vergleich mit einem konventionellen Regelungsansatz (0,47 kh/d) blieb die thermische Unbehaglichkeit mit einem Wert von 0,53 kh/d weitestgehend stabil. <br><br> Für die Nutzendeneinbindung ist zu erwähnen, dass unterschiedlichen Maßnahmen (Dashboards, JuControl, JuPower) seit 2020 durch mehr als 1300 Mitarbeitende genutzt wurden. Zur Evaluierung der Effektivität der Nutzendeneinbindung wurde basierend auf den historischen Daten vor Implementierung der Maßnahmen ein Regressionsmodell aufgesetzt, was den entstandenen Heizenergiebedarf maßgeblich als Funktion der Außentemperatur beschreibt (Fitgüte: R2 = 0,91). Dieses Modell wurde dann ebenso auf die Periode mit implementierten Maßnahmen zur Nutzendeneinbindung angewandt und mit dem tatsächlichen Energieverbrauch des Gebäudes verglichen. Es konnte gezeigt werden, dass, verglichen mit der Referenzperiode, der Heizbedarf in Abhängigkeit der Außentemperatur weniger stark anstieg und die durchschnittliche Temperatur des Pilotgebäudes durchschnittlich um 1 °C gesenkt werden konnte. Diese Effekte trugen maßgeblich zu der gemessenen Verbrauchsreduktion von 11.1 MWh pro Jahr (- 16,7 %) bei, welche die Verantwortlichen auf Grund der gleichen Systemparameter (Energetischer Zustand des Gebäudes und des Heizsystems) auf die effizientere Nutzung des Heizsystems und ein effizienteres Nutzendenverhalten zurückführen. Bei einem Gaskraftwerk zur Heizwärmebereitstellung (angenommener Emissionsfaktor von 200 g CO2e/kWhprimär; Primärenergiefaktor Erdgas = 1,1) entspricht dies einer Einsparung von ca. 2,44 t CO2e pro Jahr. Für Unterschiede in der Außentemperatur der beiden Perioden wurde dabei korrigiert, andere Einflussgrößen wurden jedoch nicht betrachtet (z.B. Wind, Solare Gewinne). Das Komfortlevel der Menschen wurde dabei nicht negativ beeinflusst. Dabei weisen die Projektverantwortlichen auf das zusätzliche Potential hin, da nur ein Fünftel der Büros in dem Gebäude für die Maßnahmen zur Nutzendeneinbindung aktiviert waren. <br><br> Die negativen Umweltwirkungen der verbauten Komponenten wurden weder für die MPC noch die Nutzendeneinbindung bilanziert. Bei der am LLEC vorzufindenden (Komponenten-)Infrastruktur besteht die Schwierigkeit zur Bewertung der negativen Wirkungen vor allem in der Allokation der Komponenten, da neben den hier beschriebenen digitalen Anwendungen noch viele weitere Prozesse und Anwendungen die gleichen Komponenten nutzen. Daher ist eine genaue Zuordnung zu einzelnen digitalen Anwendungen schwierig. Jedoch mussten für die Einzelraummessungen eine Vielzahl an batteriebetriebenen Komponenten verbaut werden (> 1800 Komponenten auf dem Campus insgesamt). Da all diese Komponenten fortwährend mit den digitalen Anwendungen Daten austauschen bzw. diese auf diese zurückgreifen, fällt ein entsprechend hoher Datenaufwand an. Alleine für die Maßnahmen zur Nutzendeneinbindung wurden in ca. 3 Jahren 364 Mio. Datensätzen erfasst und aufgearbeitet (ca. 74 GB insgesamt bzw. ca. 25 GB/a). Dabei gehen die Forschenden davon aus, dass sich der Datenaufwand bei einer noch praxisnäheren Implementierung um ca. 25% reduzieren lassen könnte. Zum einen, da die Anzahl an Datenpunkten in etwa um diese Größe reduziert werden könnte. Zum anderen, weil nach erfolgreicher Erprobung im Forschungskontext weniger Redundanzen bei den Messstellen und eine geringerer Datengranularität nötig wären. Für die MPC werden täglich ca. 300 MB an Daten auf einem OpenStack Server verarbeitet. Nur ein Bruchteil entfällt dabei auf die Erfassung der Messdaten aus den Räumen (ca. 5 MB pro Tag; 15 minütige Daten zu Raum-Temperatur, Zustände von Fenster- und Tür-Kontakten und Anzahl an Personen im Raum). Zusammengenommen fragen die Nutzendeneinbindung und die MPC jährlich virtuelle Ressourcen für ca. 124 GB nach, was überschlägig CO2-Emissionen von ca. 339 kg CO2e bedeuten würde (vergleiche Abschätzung der negativen Wirkungen durch die Datenübertragung und -verarbeitung <a href="{% url 'dataProcessing' %}">hier</a> ). <br><br> Schließlich sieht das Projekt verschiedene Anknüpfungsmöglichkeiten für künftige Forschungsvorhaben. Da MPC-Modelle zwar hohe Einsparpotenziale versprechen, jedoch gleichzeitig einen hohen Aufwand für individuelle Kalibrierung benötigen, besteht ein hoher Bedarf für die Entwicklung von einfach übertragbaren MPC-Ansätzen für kommerzielle Zwecke. Auf die vereinfachte Übertragung auf andere Gebäude zielt auch die angestrebte Verknüpfung beider Anwendungen des Projekts ab (MPC & Nutzendeneinbindung). So sind noch effizienzsteigernde Anpassungsmöglichkeiten innerhalb der Kostenfunktion des MPC möglich. Da beide Aspekte modular entwickelt wurden, ist eine zukünftige Verschränkung denkbar und sinnvoll um bspw. die Effektivität der MPC unter Einfluss von benutzerdefinierte Komforteinstellungen oder angepassten Handlungsempfehlungen an die Nutzenden zu testen. Zudem nennen die Forschenden den Bedarf für umfassendere Versuche in größeren Gebäuden unter Einbeziehung ganzzahliger Entscheidungsvariablen, sowie der Vorlauftemperaturen von Heizwasservolumenströmen (zentrale Heizungssysteme) als weitere Entwicklungsfelder. | LLEC – Verwaltungsbau: Klimaneutraler Verwaltungsbau als aktiver Teil des Living Lab Energy Campus; EnOB: LLEC: Living Lab Energy Campus | Althaus, Philipp, Florian Redder, Eziama Ubachukwu, Maximilian Mork, André Xhonneux und Dirk Müller (2022): Enhancing Building Monitoring and Control for District Energy Systems: Technology Selection and Installation within the Living Lab Energy Campus. Applied Sciences 12, Nr. 7 (Januar): 3305.;; Mork, Maximilian, Florian Redder, André Xhonneux und Dirk Müller (2023): Real-world implementation and evaluation of a Model Predictive Control framework in an office space. Journal of Building Engineering 78 (1. November): 107619.;; Ubachukwu, Eziama, Jana Pick, Lea Riebesel, Paul Lieberenz, Philipp Althaus, Dirk Müller und André Xhonneux (2023): LLEC Energy Dashboard Suite: User Engagement for Energy-Efficient Behavior Using Dashboards and Gamification. In: 36th International Conference on Efficiency, Cost, Optimization, Simulation and Environmental Impact of Energy Systems (ECOS 2023), S. 3241–3252. Veranstaltung: 36th International Conference on Efficiency, Cost, Optimization, Simulation and Environmental Impact of Energy Systems (ECOS 2023), Las Palmas De Gran Canaria, Spain. <a href="http://www.proceedings.com/069564-0291.html">http://www.proceedings.com/069564-0291.html</a>.;; United Nations Environment Programme (2021): 2021 Global Status Report for Buildings and Construction: Towards a Zero-Emission, Efficient and Resilient Buildings and Construction Sector. Nairobi, Kenya: United Nations Environment Programme.
2 | Positive Wirkung | Wohnungsunternehmen betreiben meist unterschiedliche Gebäude mit einer Vielfalt von Technologien für die Heiz- und Warmwasserversorgung. Das Potenzial zur Betriebsoptimierung dieser Heizzentralen in Mehrfamilienhäusern ist enorm. Dies sollte möglichst bedienerfreundlich und idealerweise automatisiert erfolgen. | FeBOp-MFH | FeBOp-MFH – Feldanalyse zur Betriebsoptimierung von Mehrfamilienhäusern | 03ET1573 | 05/2018 – 07/2022 | Institut für Solarenergieforschung Hameln, Klimaschutz- und Energieagentur Niedersachsen GmbH, proKlima – der enercity-Fonds, Corona SOLAR GmbH; acht niedersächsische Kooperationspartner aus der Wohnungswirtschaft | https://www.klimaschutz-niedersachsen.de/themen/waerme/FeBop.php |  |  | Betriebsoptimierung, Dashboard/Plattform | Verbrauchsminimierung, Steigerung der Materialeffizienz, Effizienzsteigerung | Informations- und Wissensvermittlung, Nudging, Austausch von Komponenten/Geräten, Umsetzung Messkonzepte/Monitoring, Automatisierung | Geringe Umweltlasen bei gleichzeitig hoher Verbreitungschance | assets/images/FeBOp_year_comparison.png | Wohnungsunternehmen betreiben meist unterschiedliche Gebäude mit einer Vielfalt von Technologien für die Heiz- und Warmwasserversorgung. Das Potenzial zur Betriebsoptimierung dieser Heizzentralen in Mehrfamilienhäusern ist enorm. Dies sollte möglichst bedienerfreundlich und idealerweise automatisiert erfolgen. Das Forschungsprojekt FeBOp-MFH zielt darauf ab, mit minimalem zusätzlichem Messaufwand, Daten der Heizzentralen mithilfe eines intelligenten Mess- und Analysesystems zu erfassen und zu analysieren. Dadurch sollen automatisierte Effizienzanalysen ermöglicht und der Betrieb jeder Heizzentrale optimiert werden. Der primäre Fokus des Projekts liegt auf der Erzielung von Energie- und CO2-Einsparungen sowie auf der Komfortsteigerung aus Sicht des Anlagenbetreibers (vereinfachte Betriebsführung). Sekundäre Ziele sind Kosteneinsparungen sowie die Verlängerung der Lebensdauer der Heiztechnik. Die erwarteten Energieeinsparungen liegen bei mindestens 10 %. Der Anwendungsbereich des Projekts erstreckt sich auf die Wärmeoptimierung im Betrieb von Mehrfamilienhäusern, die von Wohnungsunternehmen betrieben werden. Strategisch setzt das Projekt auf Monitoring, Informations- und Wissensvermittlung sowie Handlungsempfehlungen. Diese Maßnahmen richten sich hauptsächlich an die Anlagenbetreiber und nicht an die Mietenden. Es kommen zum einen die Betriebsoptimierung sowie die dafür notwendige Aufbereitung mittels Dashboards bzw. einer digitalen Plattform zum Einsatz. Hierzu werden Kennwerte wie der Nutzungsgrad unter anderem mit „adaptiven“ Benchmarks verglichen. Diese adaptiven Benchmarks nach VDI 3807-1 beziehen sich nicht nur auf das individuelle Gebäude, sondern sind besonders für das gesamte Gebäudeportfolio von Interesse. Hierbei wird der Mittelwert der besten 25 % der Gebäude mit vergleichbarer Technik und Nutzung als Benchmark verwendet. Wohnungsbauunternehmen können so die Gebäude bzw. Anlagen mit dem Benchmark vergleichen und größte Bedarfe und Potenziale für ihr eigenes Portfolio identifizieren. Diese adaptive Herangehensweise mit praktisch erreichten und somit realistischen Kennwerten ermöglicht eine kontinuierliche Anpassung der Benchmarks je nach Zeitraum und durchgeführten Modernisierungsmaßnahmen. Dadurch entsteht nicht nur eine interne Vergleichbarkeit, sondern auch die mit anderen Unternehmen und Objekten, was zu gezielten Handlungen anregen kann. | In dem Projekt FeBOp-MFH wurden gezielt die Potenziale zur Effizienzsteigerung von Heizzentralen angegangen. Die zentrale Stellschraube lag in der Effizienzanalyse des bestehenden Systems, um darauf basierend Verbesserungsmöglichkeiten zu identifizieren. Frühzeitiges Erkennen eines ineffizienten oder fehlerhaften Betriebs ermöglichte die Identifikation von geringinvestiv nutzbaren Einsparpotenzialen und den einfachen Nachweis erzielter Energie- und CO2-Einsparungen. Neben den Echtzeitdaten der Anlagen, können die Betreiber aus Monats- und Jahresberichten Ansatzpunkte für Optimierungsoptionen ableiten. Dazu werden wichtige Kennzahlen wie die Auslastung, Betriebszeiten, Temperaturverläufe, Verluste und der Nutzungsgrad der Heizzentrale dargestellt. Die im Projekt identifizierten Stellschrauben zum Heben der Effizienzpotenziale umfassten die Anpassung von Betriebszeiten und Temperaturen, das Minimieren von Zirkulationszeiten und – für einen möglichen Kessel/Heizungstausch – Hilfestellungen für eine bedarfsgerechte Dimensionierung der Heizung, was den zukünftigen Materialeinsatz minimiert und Überdimensionierungen vermeidet. In den bisherigen Untersuchungen wurde zudem die zentrale Trinkwarmwassererzeugung als häufig ineffizient identifiziert, was den Einsatz dezentraler Systeme zur Warmwasserbereitung (z.B. Wohnungsstationen) zu einer weiteren relevanten Stellschraube macht (ebenfalls im Falle möglicher Modernisierungsmaßnahmen durch die Wohnungsunternehmen). Um diese Stellschrauben zu identifizieren, werden zusätzliche Messwerte benötigt. Dazu müssen jedoch nur sehr wenige Zähler, sowie Temperatur- und Volumenstromsensoren verbaut und mit einem extra Datenlogger kommunikativ über Funk oder Kabel verbunden werden. Die minütlichen Daten werden dann auf dem Datenlogger zwischengespeichert, verschlüsselt und an einen Server versendet. Dort findet wiederum die eigentliche, automatisierte Messwertaufbereitung und -auswertung statt. Die Anlagenbetreiber*innen können die Daten sodann in Echtzeit oder aggregiert vom Server abrufen. Methodisch erfolgte die Messwertaufbereitung anhand einer Vergleichsbildung durch adaptive Benchmarks. Dadurch wird die Performance der Anlage schnell mit vergleichbaren Objekten bewertbar. Die detaillierte Aufarbeitung der eigentlichen Betriebsparameter der Heizzentrale erfolgt dann entweder individuell in Echtzeit oder in automatisierter Form der Monats- oder Jahresberichte. Die Berichte sind dabei unter anderem für den monatlichen/jährlichen Vergleich der Performance der Heizzentrale ausgelegt. Für einige Optimierungsstellschrauben werden auch automatisierte Handlungsempfehlungen gegeben. So werden die Anlagenbetreiber*innen beispielsweise darauf hingewiesen, wenn mögliche Ruhezeiten der Trinkwarmwasserzirkulation nicht ausgeschöpft werden oder die Betriebstemperaturen zu hoch sind. | Das Analysesystem des Projekts ermöglicht die Evaluierung der ermittelten Kennwerte anhand von drei Referenzszenarien (Benchmarks). Im ersten Szenario wird ein fester Referenzwert als Benchmark gesetzt, der beispielsweise für den Heizkessel nach VDI 3807-5 bestimmt werden kann. Im zweiten Szenario erfolgt der Vergleich anhand von Kennwerten aus den Vorjahren (historische Daten). Dies ist allerdings erst dann sinnvoll, wenn Betriebsdaten aus mindestens zwei Jahren vorliegen und zeitliche Trends identifiziert werden sollen. Im letzten Szenario werden Kennwerte mit den entsprechenden Kennwerten aller anderen Anlagen verglichen. Diese Werte müssen alle auf der gleichen Basis berechnet worden sein. Die Benchmark ist erst dann aussagekräftig, wenn eine größere Anzahl von Anlagen über mindestens ein Jahr untersucht wurden. Im Projekt werden folgende vier Kennwerte genutzt, um einen Überblick über relevanten Qualitäten der Wärmezentralen zu geben. Die Effizienz des Wärmeerzeugers ist von zentraler Bedeutung, da diese Komponente die zugeführte Endenergie in nutzbare Wärme wandelt. Die Wärmeerzeuger werden nach den verschiedenen Endenergieträgern Gas, Öl Holz und Strom unterschieden, nicht jedoch nach Baujahr oder Bauart. Die Effizienz der Komponente wird durch den Jahresnutzungsgrad (Jahresarbeitszahl bei Wärmepumpen) charakterisiert. Er ist definiert als Verhältnis der im Jahr zur Nutzung erzeugten Wärme zu der dem Wärmeerzeuger zugefügten Endenergie ohne erneuerbare Energien. Der nächste untersuchte Kennwert ist die Effizienz der zentralen Trinkwarmwasserversorgung. Sie gibt Aufschluss über Zirkulationsverluste und Verluste der Speicherung und Beladeleitung und ist häufig der Nutzungspfad mit der geringsten Effizienz. Die Effizienz wird über den Nutzungsgrad dargestellt und berechnet sich aus der Wärmeenergie, die im verbrauchten Trinkwarmwasser enthalten ist, dividiert durch die dem Trinkwarmwasserbereiter zugeführte Wärmemenge. Auch der Anteil lokaler erneuerbarer Energien wird betrachtet. Dieser Kennwert stellt dar, wie weit das Gebäude und die Wärmezentrale durch autarke erneuerbare Energie betrieben wird. Er wird aus dem Verhältnis der am und um das Gebäude lokal bereitgestellten erneuerbaren Energien zur Summe aller zugeführten Energien berechnet. Zuletzt werden die spezifischen CO2-Emissionen untersucht. Dieser Kennwert gibt an, welche Gesamtmenge an CO2-Emissionen durch den Wärmeverbrauch des Gebäudes erzeugt werden. Die Kennwerte „Wärmeerzeuger“ und „Trinkwarmwasserversorgung“ reflektieren die Effizienz der Anlagenteile, während die Kennwerte „lokal erzeugte erneuerbare Energien“ und „CO2-Emissionen“ die Zukunftsfähigkeit der Anlage beurteilen. Im einem Beispielobjekt des Projektes ist ein Optimierungspotential für die Effizienz des Kesselnutzungsgrades von 8 % zu erkennen, für Trinkwarmwasserversorgung wird ein Optimierungspotential von 9 % berechnet, allerdings liegt der Zielwert auf einem geringeren Niveau. Ein Anzeichen dafür, dass eine zentrale Trinkwarmwasserbereitung im Allgemeinen keine gute Effizienz aufweist, da signifikante Verteilverluste nicht vermieden werden können. Der Deutsche Verein des Gas- und Wasserfaches gibt an, dass die höchsten Effizienzen und Endenergieeinsparungen hygienisch sicher nur durch eine dezentrale Trinkwarmwasserversorgung erreicht werden können. Für den Anteil erneuerbarer Energie liegt der Zielwert dreimal so hoch wie der Messwert, was einem Potential von 300 % entspricht. Auch hier liegt der Zielwert auf einem niedrigen Niveau, da die lokale Nutzung regenerativer Energien im MFH-Bereich (Umweltwärme, Solarenergie) noch nicht stark verbreitet ist. Im Gegensatz zum gegrenzten Nutzungsgrad der zentralen Trinkwarmwasserversorgung wird der Zielwert bzw. das Potential beim Anteil der regenerativen Energien durch entsprechende Modernisierungen immer weiter Richtung 100% bewegen. Der Kennwert für die CO2-Emissionen liegt am Objekt recht nah am Zielwert, was unter Berücksichtigung des geringen Anteils lokal erzeugter regenerativer Energien auf eine Ausführung der Gebäudedämmung nach mindestens aktuellem Stand der Technik hinweist. Für die Gaskessel im Gesamtbestand mit einem Mittelwert aller Anlagen von 80 % Jahresnutzungsgrad und von den besten Anlagen mit 90 % Jahresnutzungsgrad ergibt sich eine Abweichung von 10 %. Dies stellt auch das mittlere Optimierungspotential dar. Für die zentrale Trinkwarmwasserversorgung werden ebenso Einsparpotentiale berechnet. So zeigte sich an einem Beispielgebäude, dass höhere Trinkwarmwassertemperaturen und eine deutlich geringere Auslastung im Sommer zur Senkung des Nutzungsgrades der Heizzentrale um 10 %-Punkte führen können. Damit einher geht ein gesteigerter Endenergiebedarf von mindestens 10 %. Diesen, mit wenigen Mitteln erreichten, Einsparungen bzw. den ggf. durch die Erschließung der aufgezeigten Potenziale noch darüber hinaus möglichen Verbesserungen, stehen nur geringe ökologische Wirkungen gegenüber. Den CO2-Fußabdruck für die Komponenten eines Wärmepumpensystems (1 Wassserzähler, 2 Wärmezähler, 8 kabellose Temperatursensoren, 1 Datenlogger, 1 Smart-Meter) schätzt das Projekt mittels der <a href="{% url 'components' %}">Hilfestellung</a> zu den Umweltwirkungen häufig verwendeter Komponenten auf ca. 103,3 kg CO2eq/Jahr. Auch der Datenaufwand ist mit ca. 0,3 GB/Jahr gering. Über die <a href="{% url 'dataProcessing' %}">Kennwerte</a> zu den Umweltlasten der Datenübertragung- und verarbeitung können die CO2-Emissionen auf ca. 0,8 kg CO2eq/Jahr geschätzt werden (Datenübertragung mit VDSL; Serverstandort Deutschland; Use-Case virtuelle Maschine). Bei einem Emissionsfaktor von ca. 0,5 kg CO2eq/kWh<sup><a href="#sup1">1</a></sup> müssten also nur ca. 208 kWh/a Strom eingespart werden, um die Umweltlasten ausgleichen zu können. | FeBOp-MFH – Feldanalyse zur Betriebsoptimierung von Mehrfamilienhäusern | <sup id=”sup1”><a href="#ref1">1</a></sup> Vergleiche: <a href='https://www.umweltbundesamt.de/publikationen/entwicklung-der-spezifischen-treibhausgas-10'>https://www.umweltbundesamt.de/publikationen/entwicklung-der-spezifischen-treibhausgas-10</a> abgerufen am 07.06.2024

## English
| Category | Description | Name_Digital_Application | Projektname | Funding_Label | Duration | Partner | Project_Website | Consortium | Further | Digital_applications | Goals | Strategies | Relevance | Image | Problem_Statement_and_Problem_Goals | Implementation_in_the_Project | Evaluation | Project_Name | Weiterführende Literatur
0 | Positive effect | The RLT-Opt project addresses the problem of inefficient ventilation and air-conditioning systems in German non-residential buildings. The project consortium estimates that the approximately 400,000 partial air conditioning and 600,000 medium and large ventilation systems in existing buildings consume around 40 TWh/a of electricity, which accounts for around 8% of total German consumption (as of 2022). | RLT-Opt | RLT-Opt - Holistic optimization of ventilation and air conditioning systems | 03EN1037A | 04/2021–03/2024 | FraunhoferIOSB, BUILDING Consultants + Innovators GmbH, IBDM GmbH, Effizienzbörse Deutschland GmbH | www.rlt-opt.de | https://www.iosb.fraunhofer.de/de/projekte-produkte/rlt-opt-lueftungsanlagen-klimaanlagen-optimieren/konsortium.html | https://effizienzboard.de | Operational optimization, dashboards | Providing information, increasing energy efficiency, minimizing consumption and costs, extending service life | Information and knowledge transfer; Exchange of devices; Manual adjustment of devices; Early fault detection | High positive environmental impact (energy savings) | Bild1_RLT-Opt | The RLT-Opt project addresses the problem of inefficient ventilation and air conditioning systems in German non-residential buildings. The project consortium estimates that the approximately 400,000 partial air conditioning systems and 600,000 medium and large ventilation systems in existing buildings consume around 40 TWh/a of electricity, which accounts for around 8 % of total German consumption (as of 2022). Despite this, the number of systems for which energy inspections have been carried out is low (around 25,000 systems). In these systems, high energy saving potentials are often identified through the optimization of heating, cooling and electricity consumption. In principle, however, too little data is available to date on the operating status of air conditioning systems, as monitoring components are often not installed when the systems are set up. With regard to energy inspections of HVAC systems, older studies have already recommended an optimized control strategy for approx. 50% of all systems and an expansion of sensor technology for approx. 40% of systems in order to leverage savings potential. The main problem is therefore that for most systems it is unclear whether the energy consumption during operation is necessary to achieve the desired goals, such as a certain ventilation capacity. This is where the project comes in and aims to use a mobile and stationary monitoring concept to analyze weak points in HVAC systems, identify potential savings, determine derived key figures and present them in a user-friendly way. These measures are intended to optimize operation and save energy, costs and CO2. Other goals associated with optimized system operation include increasing resource efficiency and extending the service life of the air conditioning systems. The application of the mobile monitoring system, which is used for a limited period of time and is based on a low material input, can already have a high positive environmental impact. The collected data is processed and evaluated in Excel checklists, for example, so that system operators can make informed decisions at an early stage (e.g. adapting operation, replacing components/systems, etc.). For the more comprehensive stationary monitoring system, the project relies on dashboards as a strategic tool for communicating information. Infographics on operating states and the processing of key figures are intended to enable system operators, building control technicians and energy managers to adapt system operation independently and continuously to save energy. Operation is optimized, for example, by adjusting the operating times, the volume flows of the ventilation and air conditioning systems and threshold parameters, which are essential for activating/deactivating certain operating modes. Specifically, four different properties were examined as demonstration buildings in the project: two small industrial companies, a hospital and a large office building complex. Accordingly, the technology installed is also very different and varies in complexity. The communication and division of tasks between the people involved in the properties is also very heterogeneous: The larger properties often lack contact with experts: While contact persons with comprehensive competencies and tasks are easier to reach at smaller properties and the systems can also be accessed if necessary, this often proves difficult at larger properties. | As part of the project, various approaches were pursued in order to leverage potential and increase the efficiency of the ventilation and air conditioning systems. One of the central adjustment screws was simple control optimization in accordance with the DIN EN 15232 and ISO 52120 standards. This involved an overall system analysis in order to minimize the fan's volume flow on the basis of a target/actual comparison. Needs-based adjustments to the operating times and volume flows during ongoing operation were also implemented. In addition, more extensive optimization measures were carried out based on monitoring data, for example to prevent simultaneous heating and cooling. <br><br> Two monitoring variants were used for the technical implementation. Mobile monitoring was used to record and evaluate the status quo, while stationary monitoring with permanently installed components provided additional insights into operation and enabled continuous operational optimization. Mobile monitoring requires fewer components. The resource-energy requirement of the technology for mobile monitoring is estimated to be very low in the project. It amounts to a few additional sensors and meters. Nevertheless, mobile monitoring can already achieve enormous savings, particularly with regard to the functionality and dimensioning of the systems and their operating parameters. <br><br> The implementation of stationary monitoring required additional hardware and more data. In principle, the type and number of additional components required depends heavily on the size and basic equipment of the property and the systems in place. However, by recording detailed operating states, more in-depth analyses are possible, which can then be used to tap into further savings potential. | The main positive environmental impacts targeted in the project were energy and CO2 savings. The quantification of these effects was attempted by means of a before-and-after comparison of actual energy quantities, which can extend over different periods of time (depending on the respective monitoring concept - mobile and/or stationary). In general, characteristic values for system evaluation were created based on DIN SPEC 15240 and DIN 18599. Savings were partly verified by measurement and partly evaluated using extrapolations according to general physical rules, with weighted adjustments made for weather influences. Based on this, the CO2 savings were calculated using the emission factors for energy audits published by the Federal Office of Economics and Export Control.<sup id="ref1"><a href="#footnote1">1</a></sup> <br><br> The optimization results achieved in accordance with the DIN EN 15232 and ISO 52120 standards were remarkable, with average electricity savings of > 30 % across the board. The basic adjustment of the volume flow (target/actual adjustment, adjustment of operating times, etc.) in particular is an easy measure to implement, which can be carried out using mobile monitoring - i.e. with minimal use of measurement technology and resources. For some systems, the savings achieved in this way can be significantly higher than the average 30 %. This is because the power consumption is halved if the volume flow is reduced by just 20 %. For example, the volume flow for ventilating the basement area of a sample property could be reduced by 39 %, resulting in a 78 % reduction in electricity consumption. This means that around 270 MWh or 198 tCO2eq can be saved each year. Further efficiency potential can then be tapped by fine-tuning the systems depending on room occupancy/room use. However, this requires stationary monitoring, as longer periods of time must be considered. Another positive environmental effect that goes hand in hand with the optimization of operation: due to the low usage, the systems also wear out less. This can significantly increase the service life. The project network assumes possible increases in service life of up to 10 years. Resources are therefore used for longer and emissions are avoided. Fault detection is also simplified or accelerated, which can lead to faster and more effective maintenance and servicing of the systems. Negative environmental impacts of digital applications were not included in the balance. Depending on the existing system technology and building management systems, the emissions caused by monitoring and data processing vary in the individual properties. Using the example of the large office building complex (largest property examined): here, over a hundred additional sensors (air temperature, irradiance, humidity, presence detectors, CO2, pressure), around 50 meters (electricity, volume flow, heat quantities), several communication systems (BUS systems, routers, repeaters, laptops) and several hundred meters of cable (electricity, air, LAN) for stationary monitoring were also installed. In total, this property generates 10 GB of data per year. With such comparatively complex properties, there can also be other obstacles that can reduce the effectiveness of the measures. The building management system and its accessibility (closed interfaces, lack of expert level) should be mentioned here in particular, which can make it difficult to implement the recommendations for action to optimize operations. Predictive control strategies, which could potentially result in even greater savings potential, are therefore often costly to implement. At the same time, it makes sense to support the system operators in implementing the possible operating optimization strategies (e.g. manual adjustment of the volume flow or operating times), as the project showed that in some cases there is little expertise and previous points of contact in this regard. Despite the material costs and technical and organizational hurdles, electricity savings of > 30 % were achieved across the board, even in large properties. | RLT-Opt– Lüftungs- und Klimaanlagen ganzheitlich optimieren | <sup id=”sup1”><a href="#ref1">1</a></sup> Basis für Berechnung: Emissionsfaktor Strom (Effizienzmaßnahmen) = 0,732 tCO2/MWh, aus Informationsblatt CO2-Faktoren; Bundesamt für Wirtschaft und Ausfuhrkontrolle, 2021.
1 | Positive effect | The project focuses in particular on increasing the energy efficiency of heating, cooling and air conditioning systems in office buildings while taking user satisfaction into account. Model predictive control (MPC) is used, which makes it possible to predict and automatically control non-linear system behavior. Various studies estimate energy savings of between 15 % and 50 % (Mork et al. 2023). | LLEC | LLEC - Administration building: Climate-neutral administration building as an active part of the Living Lab Energy Campus; EnOB: LLEC: Living Lab Energy Campus | 03EGB0010A;; 03ET1551A | 01/2018 – 06/2025 01/2018 – 03/2025 | Karlsruhe Institute of Technology, LOHC Technologies, suppliers: BFT Planung GmbH, Hydrogenious, Riello Power Systems GmbH, AutoPi.io ApS, be.storaged GmbH, SonnJa! GmbH | https://www.fz-juelich.de/de/llec |  |  | Operational optimization, dashboards, digital twin | Energy savings, reduced consumption, increased comfort | Control and regulation / model predictive control, gamification, information and knowledge transfer | Consumption reduction in complex building structures by users, among others | llec_logo_large_transparent | The heterogeneity of buildings, which arises, for example, as a result of different system fleets and/or usage profiles, as well as the behaviour of building users, present complex challenges when it comes to minimizing energy consumption. There is often a lack of reliable data and corresponding digital applications to adequately assess and optimize the energy consumption and efficiency of buildings. Due to their significant share of total energy consumption (30%), improving energy efficiency and reducing CO2 emissions from buildings is increasingly the focus of current research <a href="#United_Nations_Environment_2021">(United Nations Environment Programme 2021)</a>. <br><br> The Living Lab Energy Campus (LLEC) at Forschungszentrum Jülich pursues the goal of researching solutions for energy efficiency in buildings and presenting them to the public. Highly networked demonstrators show various research projects, for example on photovoltaics or energy storage. In addition, two projects are attempting to minimize energy consumption by integrating innovative technologies and approaches. The central key here is the collection and analysis of building data. Based on this, modular solutions are being designed that can be transferred to other buildings following successful testing. One focus of optimization in this regard is the development of intelligent control systems for controlling energy consumption systems in some buildings and the campus energy demonstrators. In order to counter the high heterogeneity of the buildings and parts of buildings, a large number of influencing variables must be considered. At the same time, user behaviour is being researched and used as an active means of minimizing consumption in another building. The LLEC enables the development and application of such solutions in a representative and realistic environment that allows research results to be validated. In administrative buildings in particular, influencing the intrinsic motivation of people can be essential, as it has been proven that they do not feel responsible for their influence on energy consumption as long as they do not bear the costs. Another aim of the project is to promote knowledge transfer and raise awareness of the issue of energy efficiency in buildings. The LLEC offers training courses, workshops and information events for experts, students and the interested public in order to raise awareness of energy-efficient construction and disseminate specialist knowledge. | The project focuses in particular on increasing the energy efficiency of heating, cooling and air conditioning systems in office buildings while taking user satisfaction into account. Model predictive control (MPC) is used, which makes it possible to predict and automatically control non-linear system behavior. Various studies estimate energy savings of between 15% and 50% <a href="#Mork,_Maximilian,_Florian_2023">(Mork et al. 2023)</a>. In the project, the practically implemented MPC takes into account the energy consumption for heating and lighting, thermal discomfort and potential user disturbances caused by high-frequency shading. The control system takes into account tuning parameters and comfort limits. It should be noted that the use of MPC currently requires customized modeling for each individual building, but simplifications are also being worked on in this project (e.g. easy-to-create and transferable Modelica modules). With regard to the influence of the weather, different effects such as outside temperatures / heating requirements, wind forces and solar gains were included in the control algorithms. <br><br> Independently of the MPC approaches, the researchers are working on the integration of software applications that make it possible to view energy consumption data and provide users with real-time recommendations for behavioral changes <a href="#Ubachukwu,_Eziama,_Jana_2023">(Ubachukwu et al. 2023)</a>. The "Energy Dashboard" offers employees and visitors to the LLEC an overview of heating and electricity consumption in real time at room level, among other things. "JuControl" goes one level further and enables users to map their personal preferences for the indoor climate and intervene in the control system. A gamification approach is embedded in the application, which enables comparison with other people/teams. Feedback to users is provided via a traffic light system that indicates energy consumption. The traffic light is evaluated on the basis of defined limits, measured in kilowatt hours. In addition, the application reflected an "energy reference value" that simulates what the energy consumption of the entire LLEC campus would have been if everyone had had a corresponding usage profile (ideal value). In this sense, the project differs from conventional approaches to evaluating positive environmental impacts. While the savings are normally set in reference to the status quo consumption, the reference at the LLEC asks about the ideal state that could be achieved. This is because the potential for energy savings in individual rooms can vary greatly depending on the location, type of use and personal experience of the users. These influences are taken into account by defining an ideal. The system for user involvement is supplemented by a leaderboard (in the "JuPower" application), which recognizes teams with the lowest energy consumption. Incentives for energy-efficient user behavior are also created through social interaction and "game rewards". <br><br>In order to ensure the correct measurement of data, EnOcean sensors were installed in all participating buildings to measure air quality, CO2 concentration, temperature and humidity. The data was processed using M-Bus. KNX control elements and BACnet systems were used for the automatic control of lighting, heating and sun protection. Across the entire LLEC campus, studies were carried out on the integration of over 1800 devices in 18 buildings using an information and communication platform (EnOcean: 1676 sensors and 108 actuators, KNX: 48 sensors and 36 actuators) <a href="#Althaus,_Philipp,_Florian_2022">(Althaus et al. 2022)</a>. | The researchers estimate the energy savings that can be achieved using MPC to be around 10 - 15 % across all the buildings tested. To this end, a digital twin of the buildings was operated comparatively using different control strategies. Intelligent control of the room temperature, automated window opening and adjustment of the solar shading (focus on heating/air conditioning; effects on electricity demand for lighting not included) have the greatest impact on energy savings. The solar shading is designed to make maximum use of solar heat gains and daylight in order to minimize energy consumption for heating and lighting. The measurements were able to confirm the quality of the simulations. More energy-efficient room temperature profiles were measured. However, due to a lack of meters in the individual rooms/parts of the building, it was not possible to carry out a precise comparison of the energy consumption. Quantitatively, the LLEC can confirm the high accuracy of the white-box MPC model. The Root Mean Square Error (RSME) between the measured and estimated room temperature was 0.49 °C. The efficient operation of the control system was also demonstrated. In comparison with a conventional control approach (0.47 kh/d), the thermal discomfort remained largely stable with a value of 0.53 kh/d. <br><br> In terms of user involvement, it should be noted that various measures (dashboards, JuControl, JuPower) have been used by more than 1,300 employees since 2020. To evaluate the effectiveness of user involvement, a regression model was set up based on the historical data before the measures were implemented, which describes the heating energy demand as a function of the outside temperature (fit quality: R2 = 0.91). This model was then also applied to the period with implemented measures for user involvement and compared with the actual energy consumption of the building. It was shown that, compared to the reference period, the heating demand increased less strongly depending on the outside temperature and the average temperature of the pilot building could be reduced by 1 °C on average. These effects contributed significantly to the measured reduction in consumption of 11.1 MWh per year (- 16.7 %), which those responsible attribute to the more efficient use of the heating system and more efficient user behavior due to the same system parameters (energy status of the building and the heating system). With a gas-fired power plant for heating (assumed emission factor of 200 g CO2e/kWh primary; primary energy factor natural gas = 1.1), this corresponds to a saving of approx. 2.44 t CO2e per year. Corrections were made for differences in the outside temperature between the two periods, but other influencing variables were not taken into account (e.g. wind, solar gains). The comfort level of the people was not negatively affected. The project managers point out the additional potential, as only a fifth of the offices in the building were activated for the measures to integrate users. <br><br> The negative environmental impacts of the installed components were not balanced for either the MPC or the user integration. With the (component) infrastructure found at the LLEC, the difficulty in assessing the negative impacts lies primarily in the allocation of the components, as many other processes and applications use the same components in addition to the digital applications described here. It is therefore difficult to allocate them precisely to individual digital applications. However, a large number of battery-operated components had to be installed for the individual room measurements (> 1800 components on the campus in total). As all of these components are constantly exchanging data with the digital applications or accessing them, a correspondingly high amount of data is required. For the user integration measures alone, 364 million data records were recorded and processed in around 3 years (approx. 74 GB in total or approx. 25 GB/a). The researchers assume that the amount of data could be reduced by approx. 25% with an even more practical implementation. On the one hand, because the number of data points could be reduced by approximately this amount. Secondly, because after successful testing in a research context, fewer redundancies in the measuring points and less data granularity would be required. Around 300 MB of data is processed daily on an OpenStack server for the MPC. Only a fraction of this is used to record measurement data from the rooms (approx. 5 MB per day; 15 minutes of data on room temperature, the status of window and door contacts and the number of people in the room). Taken together, user integration and the MPC require virtual resources for approx. 124 GB per year, which would mean estimated CO2 emissions of approx. 339 kg CO2e (see estimate of the negative effects of data transmission and processing <a href="{% url 'dataProcessing' %}">here</a> ). <br><br> Finally, the project sees various opportunities for future research projects. As MPC models promise high savings potential, but at the same time require a great deal of effort for individual calibration, there is a great need for the development of easily transferable MPC approaches for commercial purposes. The intended linking of the two applications of the project (MPC & user integration) is also aimed at simplified transfer to other buildings. This means that efficiency-enhancing customization options are still possible within the MPC cost function. As both aspects were developed on a modular basis, a future linkage is conceivable and makes sense, for example to test the effectiveness of the MPC under the influence of user-defined comfort settings or customized recommendations for action to the users. The researchers also cite the need for more comprehensive tests in larger buildings, including integer decision variables and the flow temperatures of heating water volume flows (central heating systems) as further areas of development. | LLEC – Verwaltungsbau: Klimaneutraler Verwaltungsbau als aktiver Teil des Living Lab Energy Campus; EnOB: LLEC: Living Lab Energy Campus | Althaus, Philipp, Florian Redder, Eziama Ubachukwu, Maximilian Mork, André Xhonneux und Dirk Müller (2022): Enhancing Building Monitoring and Control for District Energy Systems: Technology Selection and Installation within the Living Lab Energy Campus. Applied Sciences 12, Nr. 7 (Januar): 3305.;; Mork, Maximilian, Florian Redder, André Xhonneux und Dirk Müller (2023): Real-world implementation and evaluation of a Model Predictive Control framework in an office space. Journal of Building Engineering 78 (1. November): 107619.;; Ubachukwu, Eziama, Jana Pick, Lea Riebesel, Paul Lieberenz, Philipp Althaus, Dirk Müller und André Xhonneux (2023): LLEC Energy Dashboard Suite: User Engagement for Energy-Efficient Behavior Using Dashboards and Gamification. In: 36th International Conference on Efficiency, Cost, Optimization, Simulation and Environmental Impact of Energy Systems (ECOS 2023), S. 3241–3252. Veranstaltung: 36th International Conference on Efficiency, Cost, Optimization, Simulation and Environmental Impact of Energy Systems (ECOS 2023), Las Palmas De Gran Canaria, Spain. <a href="http://www.proceedings.com/069564-0291.html">http://www.proceedings.com/069564-0291.html</a>.;; United Nations Environment Programme (2021): 2021 Global Status Report for Buildings and Construction: Towards a Zero-Emission, Efficient and Resilient Buildings and Construction Sector. Nairobi, Kenya: United Nations Environment Programme.
2 | Positive effect | Housing companies usually operate different buildings with a variety of technologies for heating and hot water supply. The potential for optimizing the operation of these central heating systems in apartment buildings is enormous. This should be as user-friendly as possible and ideally automated. | FeBOp-MFH | FeBOp-MFH - Field analysis for optimizing the operation of multi-family houses | 03ET1573 | 05/2018 – 07/2022 | Institut für Solarenergieforschung Hameln, Klimaschutz- und Energieagentur Niedersachsen GmbH, proKlima - der enercity-Fonds, Corona SOLAR GmbH; eight cooperation partners from the housing industry in Lower Saxony | https://www.klimaschutz-niedersachsen.de/themen/waerme/FeBop.php |  |  | Operational optimization, dashboard/platform | Minimizing consumption, increasing material efficiency, increasing efficiency | Information and knowledge transfer, nudging, replacement of components/devices, implementation of measurement concepts/monitoring, automation | Low environmental lases with a high chance of spreading | FeBOp_Jahresvgl_groß | Housing companies usually operate different buildings with a variety of technologies for heating and hot water supply. The potential for optimizing the operation of these central heating systems in apartment buildings is enormous. This should be as user-friendly as possible and ideally automated. The FeBOp-MFH research project aims to record and analyze data from the central heating systems using an intelligent measurement and analysis system with minimal additional measurement effort. This should enable automated efficiency analyses and optimize the operation of each heating system. The primary focus of the project is on achieving energy and CO2 savings as well as increasing comfort from the system operator's point of view (simplified operational management). Secondary objectives are cost savings and extending the service life of the heating technology. The expected energy savings are at least 10 %. The scope of the project extends to heat optimization in the operation of apartment buildings operated by housing companies. Strategically, the project focuses on monitoring, information and knowledge transfer as well as recommendations for action. These measures are mainly aimed at the system operators and not the tenants. On the one hand, operational optimization and the necessary processing by means of dashboards or a digital platform are used. For this purpose, key values such as the degree of utilization are compared with "adaptive" benchmarks, among other things. These adaptive benchmarks in accordance with VDI 3807-1 not only relate to the individual building, but are of particular interest for the entire building portfolio. The average value of the best 25% of buildings with comparable technology and use is used as a benchmark. Housing companies can thus compare the buildings and facilities with the benchmark and identify the greatest needs and potential for their own portfolio. This adaptive approach with practically achieved and therefore realistic characteristic values enables continuous adjustment of the benchmarks depending on the period and modernization measures carried out. This not only creates internal comparability, but also comparability with other companies and properties, which can encourage targeted action. | In the FeBOp-MFH project, the potential for increasing the efficiency of central heating systems was specifically addressed. The main focus was on analyzing the efficiency of the existing system in order to identify potential improvements. Early detection of inefficient or faulty operation made it possible to identify potential savings that could be exploited with little investment and provide simple proof of the energy and CO2 savings achieved. In addition to the real-time data from the systems, the operators can derive starting points for optimization options from monthly and annual reports. For this purpose, important key figures such as capacity utilization, operating times, temperature curves, losses and the efficiency of the heating system are displayed. The levers identified in the project for leveraging efficiency potential included adjusting operating times and temperatures, minimizing circulation times and - for a possible boiler/heating system replacement - assistance in sizing the heating system to meet demand, which minimizes the future use of materials and avoids oversizing. Previous studies have also identified centralized domestic hot water production as frequently inefficient, which makes the use of decentralized systems for water heating (e.g. home stations) another relevant factor (also in the case of possible modernization measures by housing companies). Additional measured values are required to identify these adjusting screws. However, only a very small number of meters, as well as temperature and volume flow sensors, need to be installed and connected to an extra data logger via radio or cable. The minute-by-minute data is then temporarily stored on the data logger, encrypted and sent to a server. This is where the actual, automated processing and evaluation of the measured values takes place. The system operators can then retrieve the data from the server in real time or in aggregated form. Methodically, the measured values are processed on the basis of comparative formation using adaptive benchmarks. This allows the performance of the system to be quickly evaluated against comparable objects. The detailed processing of the actual operating parameters of the heating system then takes place either individually in real time or in the automated form of monthly or annual reports. Among other things, the reports are designed for monthly/annual comparisons of the heating center's performance. Automated recommendations for action are also provided for some optimization settings. For example, the system operators are notified if possible rest periods for the domestic hot water circulation are not fully utilized or if the operating temperatures are too high. | The project's analysis system makes it possible to evaluate the determined characteristic values using three reference scenarios (benchmarks). In the first scenario, a fixed reference value is set as a benchmark, which can be determined, for example, for the boiler in accordance with VDI 3807-5. In the second scenario, the comparison is made on the basis of characteristic values from previous years (historical data). However, this only makes sense if operating data from at least two years is available and trends over time are to be identified. In the last scenario, characteristic values are compared with the corresponding characteristic values of all other plants. These values must all have been calculated on the same basis. The benchmark is only meaningful if a large number of systems have been examined over at least one year. The following four parameters are used in the project to provide an overview of the relevant qualities of the central heating plants. The efficiency of the heat generator is of central importance, as this component converts the supplied final energy into usable heat. The heat generators are differentiated according to the various final energy sources gas, oil, wood and electricity, but not according to year of construction or type of construction. The efficiency of the component is characterized by the annual efficiency factor (seasonal performance factor for heat pumps). It is defined as the ratio of the heat generated for use in a year to the final energy supplied to the heat generator without renewable energies. The next parameter examined is the efficiency of the central domestic hot water supply. It provides information about circulation losses and losses in the storage and loading pipe and is often the utilization path with the lowest efficiency. The efficiency is represented by the degree of utilization and is calculated by dividing the thermal energy contained in the domestic hot water consumed by the amount of heat supplied to the domestic hot water heater. The proportion of local renewable energies is also taken into account. This characteristic value represents the extent to which the building and the central heating system are powered by self-sufficient renewable energy. It is calculated from the ratio of the renewable energy provided locally in and around the building to the total of all energy supplied. Finally, the specific CO2 emissions are examined. This parameter indicates the total amount of CO2 emissions generated by the building's heat consumption. The "heat generator" and "domestic hot water supply" parameters reflect the efficiency of the system components, while the "locally generated renewable energy" and "CO2 emissions" parameters assess the sustainability of the system. In one example object of the project, an optimization potential for the efficiency of the boiler efficiency of 8 % can be seen, for domestic hot water supply an optimization potential of 9 % is calculated, although the target value is at a lower level. This is an indication that central domestic hot water preparation is generally not very efficient, as significant distribution losses cannot be avoided. The German Technical and Scientific Association for Gas and Water states that the highest levels of efficiency and final energy savings can only be achieved hygienically with a decentralized domestic hot water supply. The target value for the proportion of renewable energy is three times as high as the measured value, which corresponds to a potential of 300 %. Here too, the target value is at a low level, as the local use of renewable energy in the MFH sector (environmental heat, solar energy) is not yet widespread. In contrast to the limited degree of utilization of the central domestic hot water supply, the target value or potential for the share of renewable energies will continue to move towards 100% through appropriate modernization. The characteristic value for CO2 emissions at the property is very close to the target value, which, taking into account the low proportion of locally generated renewable energy, indicates that the building insulation is at least state of the art. For the gas boilers in the overall portfolio with an average value of all systems of 80 % annual efficiency and the best systems with 90 % annual efficiency, there is a deviation of 10 %. This also represents the average optimization potential. Savings potentials are also calculated for the central domestic hot water supply. An example building showed that higher domestic hot water temperatures and significantly lower utilization in summer can lead to a reduction in the efficiency of the central heating system by 10 percentage points. This is accompanied by an increased final energy requirement of at least 10 %. These savings, which can be achieved with few resources, or the improvements that may be possible by tapping into the potential identified, are offset by only minor ecological effects. The CO2 footprint for the components of a heat pump system (1 water meter, 2 heat meters, 8 wireless temperature sensors, 1 data logger, 1 smart meter) is estimated by the project using the <a href="{% url 'components' %}">help</a> on the environmental impact of frequently used components at approx. 103.3 kg CO2eq/year. The amount of data required is also low at approx. 0.3 GB/year. Using the <a href="{% url 'dataProcessing' %}">key figures</a> on the environmental impact of data transmission and processing, the CO2 emissions can be estimated at approx. 0.8 kg CO2eq/year (data transmission with VDSL; server location Germany; use case virtual machine). With an emission factor of approx. 0.5 kg CO2eq/kWh<sup><a href="#sup1">1</a></sup>, only approx. 208 kWh/a of electricity would have to be saved in order to offset the environmental impact. | FeBOp-MFH – Feldanalyse zur Betriebsoptimierung von Mehrfamilienhäusern | <sup id=”sup1”><a href="#ref1">1</a></sup> Vergleiche: <a href='https://www.umweltbundesamt.de/sites/default/files/medien/11850/publikationen/23_2024_cc_strommix.pdf'>https://www.umweltbundesamt.de/sites/default/files/medien/11850/publikationen/23_2024_cc_strommix.pdf</a>